## Slide 1: PUF in closet, normal ventilation

## Slide 2: Validation of FDS modelling
Prescribed HRR
Simple HVAC
Local / bulk leakage

## Slide 3: Additional validation data
FOA experiments by Hägglund et al. 1996 and 1998.
Heptane pool fires in concrete enclosure.
No HRR measurement.

## Slide 4: Summary

## Slide 5: Apartment case study
Three air-tightness levels
  Traditional: q50 = 3.0 m3/m2h
  Normal: q50 = 1.5 m3/m2h
  Near-zero: q50 = 0.75 m3/m2h
HRR: t2-fires medium – ultra-fast
Damper configurations:
  No dampers
  Only inlet branch closed
  Both inlet and outlet closed
Fan configurations
  On
  Off and open
  Off and outside damper closed

## Slide 6: Peak pressures with medium fire

## Slide 7: Peak pressures with fast fires

## Slide 8: Smoke spreading to neighbours

## Slide 9: Smoke spreading: visibility
NO SMOKE

## Slide 10: Pressure management
Chart: Fast Fire, Near-Zero Envelope, Damper = Off
| 0 | 1E-3 | 5.0000000000000001E-3 | 0.01 | 0.05 | 0.08 | 0.1
 | 2314.1444 | 1844.6752 | 895.694 | 470.6753 | 46.5208 | 20.3801 | 13.5679
100 Pa would require 0.0425 m2 (D = 230 mm)
leak area.
1500 Pa threshold would require 0.002 m2 (D = 50 mm) total leak area.

## Slide 11: Issues with the HVAC system modelling
Real systems are too complex for ”engineering” the model.
Fan units are much more than just a fan. Pressure losses of the fan unit can dominate.
Real systems are always tuned and balanced for normal mode of operation. We can do the same for the FDS model, but a better tool would help.